# Genset Control – Test Specification (EXAMPLE, anonymized)

## Genset System Availability after Power Cycle

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Check the HMI status page. | HMI shows 'System ready'. No alarms are active. |
| 2 | Switch off the 24 V control supply. | HMI and control system are switched off. |
| 3 | Wait 10 s and switch on the 24 V control supply. | Control system starts. HMI shows 'Starting'. |
| 4 | Measure the time until the HMI shows 'System ready'. | HMI shows 'System ready' within 60 s. No alarms are active. |

## Engine Start from HMI in Remote Mode

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Set the local/remote selector to REMOTE. | HMI shows 'Remote mode'. |
| 2 | Press START on the HMI. | Engine cranks and starts. HMI shows 'Engine running'. |
| 3 | Check the alarm list. | No alarms are active. |

## Start Request Rejected During Active Shutdown Alarm

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Trigger shutdown alarm A050 'Emergency stop' via the emergency stop button. | Alarm A050 is displayed. Engine is not running. |
| 2 | Press START on the HMI. | Start request is rejected. Engine does not crank. |
| 3 | Release the emergency stop button and acknowledge alarm A050. | Alarm A050 is cleared. HMI shows 'System ready'. |