# System Availability after Power Cycle

## Start-Up Failure Alarm When Operational State Not Reached

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Prevent the control system from reaching operational state ([TBD] method). | Start-up delay condition is active. |
| 2 | Switch off the 24 V control supply. | HMI and control system are switched off. |
| 3 | Wait 10 s and switch on the 24 V control supply. | Control system starts. HMI shows 'Starting'. |
| 4 | Wait 60 s after switching on the 24 V control supply. | Alarm A010 'Control system start-up failed' is displayed. HMI does not show 'System ready'. |

# Battery Voltage Monitoring

## No Battery Warning in Normal Voltage Range

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Set the battery supply voltage to 25.4 V (normal class 22.0–28.8 V). | No battery warning is displayed. |
| 2 | Check the alarm list. | Neither W021 nor W022 is active. |

## Low Battery Voltage Warning and Automatic Reset

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Set the battery supply voltage to 25.4 V. | No battery warning is displayed. |
| 2 | Reduce the battery supply voltage to 20.0 V (low class < 22.0 V). | Warning W021 'Low battery voltage' is displayed. |
| 3 | Increase the battery supply voltage to 25.4 V and wait 5 s. | Warning W021 is cleared automatically. |

## High Battery Voltage Warning and Automatic Reset

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Set the battery supply voltage to 25.4 V. | No battery warning is displayed. |
| 2 | Increase the battery supply voltage to 30.0 V (high class > 28.8 V). | Warning W022 'High battery voltage' is displayed. |
| 3 | Reduce the battery supply voltage to 25.4 V and wait 5 s. | Warning W022 is cleared automatically. |

## Battery Voltage Warning Thresholds at Range Boundaries

| # | Actions | Expected Results |
| --- | --- | --- |
| 1 | Set the battery supply voltage to 22.0 V. | No battery warning is displayed. |
| 2 | Reduce the battery supply voltage to 22.0 V minus [TBD] V. | Warning W021 'Low battery voltage' is displayed. |
| 3 | Set the battery supply voltage to 28.8 V and wait 5 s. | No battery warning is displayed. |
| 4 | Increase the battery supply voltage to 28.8 V plus [TBD] V. | Warning W022 'High battery voltage' is displayed. |
| 5 | Set the battery supply voltage to 25.4 V and wait 4 s. | Warning W022 is still displayed. |
| 6 | Wait a further 1 s. | Warning W022 is cleared automatically. |