## Manual fields
Title (Text heading) | ShortDescription | Preconditions | Type | Origin | Source TC | Requirement refs | Open points
Genset System Availability after Power Cycle | Operational system after boot up | - Plant ready for operations. - No alarms. - Engine is not running. | positive | REUSED | Genset System Availability after Power Cycle | 1 System Availability after Power Cycle
Start-Up Failure Alarm When Operational State Not Reached | Alarm A010 if start-up exceeds 60 s | - Plant ready for operations. - No alarms. - Engine is not running. - Means to delay control system start-up available (e.g. disconnected I/O module). | negative | ADAPTED | Genset System Availability after Power Cycle | 1 System Availability after Power Cycle | Requirement does not define how a start-up failure can be provoked in the test setup.
No Battery Warning in Normal Voltage Range | No warning at 22.0–28.8 V | - Plant ready for operations. - No alarms. - Starter battery replaced by adjustable power supply. | positive | NEW |  | 2 Battery Voltage Monitoring
Low Battery Voltage Warning and Automatic Reset | W021 below 22.0 V, cleared after 5 s normal | - Plant ready for operations. - No alarms. - Starter battery replaced by adjustable power supply. | negative | NEW |  | 2 Battery Voltage Monitoring
High Battery Voltage Warning and Automatic Reset | W022 above 28.8 V, cleared after 5 s normal | - Plant ready for operations. - No alarms. - Starter battery replaced by adjustable power supply. | negative | NEW |  | 2 Battery Voltage Monitoring
Battery Voltage Warning Thresholds at Range Boundaries | Warning behaviour at 22.0 V and 28.8 V | - Plant ready for operations. - No alarms. - Starter battery replaced by adjustable power supply with [TBD] V resolution. | edge | NEW |  | 2 Battery Voltage Monitoring | Measurement resolution / tolerance of the voltage thresholds is not specified.