# EXAMPLE – Generator Set Control Requirements (anonymized)

# 1 System Availability after Power Cycle

After restoration of the 24 V control supply, the control system shall reach operational state within 60 s and report 'System ready' on the HMI.

If operational state is not reached within 60 s, alarm A010 'Control system start-up failed' shall be raised.

# 2 Battery Voltage Monitoring

The control system shall monitor the starter battery voltage.

| Range | Voltage | Reaction |
| --- | --- | --- |
| Low | < 22.0 V | Warning W021 'Low battery voltage' |
| Normal | 22.0 V – 28.8 V | No warning |
| High | > 28.8 V | Warning W022 'High battery voltage' |

A warning shall be cleared automatically when the voltage returns to the normal range for at least 5 s.